## COWs List
COW ID | Power Source | Shelter Type | Location | Latitude | Longitude | Single Generator Capacity KVA | Single Generator Working-hours Hours | SEC Meter Capacity Amp | Backup Generator Capacity KVA | Backup Generator Working-hours Hours | Rectifier Capacity KW | AC1 Capacity Btu/h | AC1 Age Years | AC2 Capacity Btu/h | AC2 Age Years | Batteries Capacity Ah | Number of Strings Number | Batteries Age Years | Avrage lead-acid Charge Rate c-rate A/Ah | Avrage Lithium disCharge Rate c-rate A/Ah | Telecom Load Outside KW | Telecom Load inside Shelter KW | Telecom Load All KW | Telecom load heat dissipation KBtu/h | Prime Generator Net Power output KW | Prime SEC Net Power Output KW | Backup Generator Net Power Output KW | Rectifier Net Power Output KW | AC1 Net Cooling Capacity KBtu/h | AC1 Net Power Demand KW | AC2 Net Cooling Capacity KBtu/h | AC2 Net Power Demand KW | Batteries Strings MAX useful capacity Ah | Batteries Strings MAX useful capacity KWh | Batteries Strings MAX useful Time Hours | Batteries Strings Max Charging Current Amp | Batteries Strings Max Charging Power KW | Batteris Strings Min Charing Time Hours | Batteries Strings Max DisCharging Current Amp | Batteries Strings Max DisCharging PowerKW | Batteris Strings Min DisCharing Time Hours | Calculated Discharge Current Amp | Connected Technology
CWN105 | SB | Shelter | Arafat | 21.3562 | 39.9848 | 0 | 0 | 100 | 30 | 0 | 18 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 20.88 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1 hr 15 min | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 240 | 2G/4G
CWN923 | DG | Shelter | Arafat | 21.3613 | 39.9739 | 45 | 0 | 0 | 35 | 0 | 22 | 36000 | 0 | 36000 | 0 | 190 | 5 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 24.36 | 22 | 29880 | 2.5021 | 29880 | 2.5021 | 475 | 23.75 | 1 hr 24 min | 275 | 1.76 | 1.7273 | 95 | 4.75 | 5 | 340 | 2G/4G/5G
CWN991 | SB | Shelter | Arafat | 21.3722 | 39.9383 | 0 | 0 | 100 | 30 | 0 | 18 | 48000 | 0 | 48000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 20.88 | 18 | 39840 | 3.3361 | 39840 | 3.3361 | 400 | 20 | 1 hr 40 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240 | 2G/4G
CWN777 | DG | Shelter | Mina | 21.3959 | 39.8997 | 35 | 0 | 0 | 25 | 0 | 16 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 24.36 | 0 | 17.4 | 16 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 40 min | 200 | 1.28 | 2 | 80 | 4 | 5 | 240 | 2G/4G
CWN108 | SB | Shelter | Arafat | 21.3492 | 39.9837 | 0 | 0 | 100 | 30 | 0 | 18 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 20.88 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1 hr 15 min | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 240 | 2G/4G
CWN087 | SB | Shelter | Arafat | 21.3569 | 39.9778 | 0 | 0 | 70 | 35 | 0 | 21 | 36000 | 0 | 36000 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 21.896 | 24.36 | 21 | 29880 | 2.5021 | 29880 | 2.5021 | 380 | 19 | 1 hr 35 min | 262.5 | 1.68 | 1.4476 | 76 | 3.8 | 5 | 240 | 2G/4G
CWN075 | SB | Shelter | Arafat | 21.347 | 39.9574 | 0 | 0 | 100 | 35 | 0 | 21.6 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 21.6 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 40 min | 270 | 1.728 | 1.4815 | 80 | 4 | 5 | 240 | 2G/4G
CWN072 | SB | Shelter | Arafat | 21.342 | 39.976 | 0 | 0 | 100 | 40 | 0 | 22 | 36000 | 0 | 36000 | 0 | 200 | 5 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 27.84 | 22 | 29880 | 2.5021 | 29880 | 2.5021 | 500 | 25 | 1 hr 28 min | 275 | 1.76 | 1.8182 | 100 | 5 | 5 | 340 | 2G/4G
CWN078 | SB | Shelter | Arafat | 21.3405 | 39.9955 | 0 | 0 | 100 | 35 | 0 | 16.2 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 16.2 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 40 min | 202.5 | 1.296 | 1.9753 | 80 | 4 | 5 | 240 | 2G/4G
CWN084 | SB | Shelter | Arafat | 21.3425 | 39.9622 | 0 | 0 | 100 | 35 | 0 | 21 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 21 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 20 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 300 | 2G/4G/5G
CWN085 | SB | Shelter | Arafat | 21.3668 | 39.9644 | 0 | 0 | 100 | 35 | 0 | 18 | 36000 | 0 | 36000 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 380 | 19 | 1 hr 35 min | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 240 | 2G/4G
CWN073 | SB | Shelter | Arafat | 21.3738 | 39.9865 | 0 | 0 | 100 | 35 | 0 | 19 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 19 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 11 min | 237.5 | 1.52 | 1.6842 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN093 | SB | Shelter | Arafat | 21.3568 | 39.9353 | 0 | 0 | 200 | 45 | 0 | 22 | 36000 | 0 | 36000 | 0 | 200 | 8 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 62.56 | 31.32 | 22 | 29880 | 2.5021 | 29880 | 2.5021 | 800 | 40 | 2 hr 40 min | 275 | 1.76 | 2.9091 | 160 | 8 | 5 | 300 | 2G/4G/5G
CWN996 | DG | Outdoor | Arafat | 39.9806 | 39.9806 | 45 | 0 | 0 | 20 | 0 | 20 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 13.92 | 20 | 8466 | 1.4179 | 0 | 0 | 380 | 19 | 1 hr 7 min | 250 | 1.6 | 1.52 | 76 | 3.8 | 5 | 340 | 2G/4G
CWN102 | SB | Shelter | Arafat | 21.359 | 39.9569 | 0 | 0 | 100 | 45 | 0 | 19.2 | 36000 | 0 | 36000 | 0 | 200 | 8 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 31.32 | 19.2 | 29880 | 2.5021 | 29880 | 2.5021 | 800 | 40 | 2 hr 40 min | 240 | 1.536 | 3.3333 | 160 | 8 | 5 | 300 | 2G/4G/5G
CWN956 | SB | Outdoor | Arafat | 21.3704 | 39.9854 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240 | 2G/4G
CWN980 | SB | Outdoor | Arafat | 21.3718 | 39.986 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240 | 2G/4G
CWN951 | SB | Outdoor | Arafat | 21.3626 | 39.9691 | 0 | 0 | 100 | 25 | 0 | 15 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 15 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 187.5 | 1.2 | 2.1333 | 80 | 4 | 5 | 240 | 2G/4G
CWN020 | SB | Outdoor | Arafat | 21.3505 | 39.9681 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 20 min | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 300 | 2G/4G/5G
CWN203 | SB | Outdoor | Arafat | 21.3547 | 39.9862 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 11 min | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN914 | SB | Outdoor | Arafat | 21.3654 | 39.9717 | 0 | 0 | 100 | 25 | 0 | 15 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 15 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 187.5 | 1.2 | 2.1333 | 80 | 4 | 5 | 240 | 2G/4G
CWN015 | SB | Outdoor | Arafat | 21.3776 | 39.9868 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240 | 2G/4G
CWN212 | SB | Outdoor | Arafat | 21.3661 | 39.9841 | 0 | 0 | 100 | 35 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 21 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 20 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 300 | 2G/4G/5G
CWN992 | SB | Outdoor | Muzdalifah | 21.3892 | 39.9069 | 0 | 0 | 60 | 25 | 0 | 15 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 18.768 | 17.4 | 15 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 187.5 | 1.2 | 2.1333 | 80 | 4 | 5 | 240 | 2G/4G
CWN960 | SB | Outdoor | Arafat | 21.3471 | 39.9926 | 0 | 0 | 100 | 45 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 21 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G
CWN984 | SB | Outdoor | Arafat | 21.3488 | 39.9957 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 40 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240 | 2G/4G
CWN906 | SB | Outdoor | Arafat | 21.3762 | 39.9823 | 0 | 0 | 100 | 30 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 20.88 | 18 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 20 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 300 | 2G/4G/5G
CWN214 | SB | Outdoor | Muzdalifah | 21.3919 | 39.9037 | 0 | 0 | 100 | 35 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 21 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN903 | SB | Outdoor | Arafat | 21.3599 | 39.948 | 0 | 0 | 100 | 45 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 31.32 | 18 | 8466 | 2.1268 | 0 | 0 | 400 | 20 | 1 hr 20 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 300 | 2G/4G/5G
CWN036 | SB | Shelter | Arafat | 21.3799 | 39.9441 | 0 | 0 | 100 | 45 | 0 | 18 | 48000 | 0 | 48000 | 0 | 190 | 5 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 31.32 | 18 | 39840 | 3.3361 | 39840 | 3.3361 | 475 | 23.75 | 1 hr 35 min | 225 | 1.44 | 2.1111 | 95 | 4.75 | 5 | 300 | 2G/4G/5G
CWN080 | DG | Shelter | Arafat | 39.9901 | 39.9901 | 45 | 0 | 0 | 35 | 0 | 21.6 | 36000 | 0 | 36000 | 0 | 190 | 8 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 24.36 | 21.6 | 29880 | 2.5021 | 29880 | 2.5021 | 760 | 38 | 2 hr 14 min | 270 | 1.728 | 2.8148 | 152 | 7.6 | 5 | 340 | 2G/4G/5G
CWN907 | DG | Outdoor | Mina | 39.9087 | 39.9087 | 35 | 0 | 0 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 24.36 | 0 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 20 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 300 | 2G/4G
CWN074 | SB | Shelter | Muzdalifah | 21.3884 | 39.9024 | 0 | 0 | 100 | 35 | 0 | 18.9 | 36000 | 0 | 36000 | 0 | 200 | 2 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 18.9 | 29880 | 2.5021 | 29880 | 2.5021 | 200 | 10 | 0 hr 50 min | 236.25 | 1.512 | 0.84656 | 40 | 2 | 5 | 240 | 2G/4G
CWN978 | SB | Shelter | Mina | 21.4218 | 39.8919 | 0 | 0 | 100 | 30 | 0 | 18 | 48000 | 0 | 48000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 20.88 | 18 | 39840 | 3.3361 | 39840 | 3.3361 | 300 | 15 | 1 hr 15 min | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 240 | 2G/4G
CWN998 | DG | Outdoor | Makkah Remote | 21.6472 | 40.3892 | 45 | 0 | 0 | 25 | 0 | 30 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 17.4 | 30 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 11 min | 375 | 2.4 | 1.0667 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN068 | SB | Shelter | Muzdalifah | 21.3922 | 39.9124 | 0 | 0 | 100 | 35 | 0 | 24.3 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 24.3 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1 hr 0 min | 303.75 | 1.944 | 0.98765 | 60 | 3 | 5 | 300 | 2G/4G/5G
CWN089 | SB | Shelter | Muzdalifah | 21.3842 | 39.9108 | 0 | 0 | 100 | 35 | 0 | 15 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 15 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1 hr 15 min | 187.5 | 1.2 | 1.6 | 60 | 3 | 5 | 240 | 2G/4G
CWN079 | SB | Shelter | Muzdalifah | 21.3615 | 39.9179 | 0 | 0 | 100 | 45 | 0 | 21 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 21 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN104 | SB | Shelter | Muzdalifah | 21.3766 | 39.919 | 0 | 0 | 100 | 45 | 0 | 18 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 31.32 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1 hr 0 min | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 300 | 2G/4G/5G
CWN066 | SB | Shelter | Muzdalifah | 21.3906 | 39.92 | 0 | 0 | 100 | 35 | 0 | 21.6 | 36000 | 0 | 36000 | 0 | 200 | 2 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 21.6 | 29880 | 2.5021 | 29880 | 2.5021 | 200 | 10 | 0 hr 50 min | 270 | 1.728 | 0.74074 | 40 | 2 | 5 | 240 | 2G/4G
CWN967 | DG | Outdoor | Makkah Remote | 21.631 | 40.4272 | 35 | 0 | 0 | 20 | 0 | 33 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.56 | 1.44 | 15 | 4913.28 | 24.36 | 0 | 13.92 | 33 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 20 min | 412.5 | 2.64 | 0.9697 | 80 | 4 | 5 | 300 | 2G/4G/5G
CWN202 | SB | Outdoor | Muzdalifah | 21.397 | 39.9035 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1 hr 35 min | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 240 | 2G/4G
CWN922 | SB | Outdoor | Muzdalifah | 21.4041 | 39.9161 | 0 | 0 | 100 | 25 | 0 | 15 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 15 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 187.5 | 1.2 | 2.1333 | 80 | 4 | 5 | 240 | 2G/4G
CWN201 | SB | Outdoor | Mina | 21.4207 | 39.881 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1 hr 16 min | 300 | 1.92 | 1.2667 | 76 | 3.8 | 5 | 300 | 2G/4G/5G
CWN300 | SB | Outdoor | Muzdalifah | 21.3866 | 39.8971 | 0 | 0 | 100 | 45 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 21 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN004 | SB | Outdoor | Muzdalifah | 21.3877 | 39.8962 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 11 min | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN970 | DG | Outdoor | Mina | 39.9059 | 39.9059 | 45 | 0 | 0 | 20 | 0 | 18 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 31.32 | 0 | 13.92 | 18 | 8466 | 1.4179 | 0 | 0 | 380 | 19 | 1 hr 16 min | 225 | 1.44 | 1.6889 | 76 | 3.8 | 5 | 300 | 2G/4G/5G
CWN206 | DG | Outdoor | Muzdalifah | 39.9283 | 39.9283 | 35 | 0 | 0 | 20 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 24.36 | 0 | 13.92 | 24 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 20 min | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 300 | 2G/4G
CWN301 | SB | Outdoor | Muzdalifah | 21.3869 | 39.8995 | 0 | 0 | 100 | 35 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 18 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 20 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 300 | 2G/4G/5G
CWN008 | SB | Outdoor | Arafat | 21.3514 | 39.9813 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 5 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 2.1268 | 0 | 0 | 500 | 25 | 1 hr 28 min | 300 | 1.92 | 1.6667 | 100 | 5 | 5 | 340 | 2G/4G/5G
CWN032 | SB | Outdoor | Muzdalifah | 21.36 | 39.9123 | 0 | 0 | 100 | 45 | 0 | 19 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 19 | 8466 | 2.1268 | 0 | 0 | 380 | 19 | 1 hr 7 min | 237.5 | 1.52 | 1.6 | 76 | 3.8 | 5 | 340 | 2G/4G/5G
CWN972 | SB | Outdoor | Muzdalifah | 21.3607 | 39.9162 | 0 | 0 | 100 | 45 | 0 | 21 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 21 | 8466 | 2.1268 | 0 | 0 | 380 | 19 | 1 hr 7 min | 262.5 | 1.68 | 1.4476 | 76 | 3.8 | 5 | 340 | 2G/4G/5G
CWN211 | SB | Outdoor | Muzdalifah | 21.3866 | 39.9113 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 380 | 19 | 1 hr 7 min | 300 | 1.92 | 1.2667 | 76 | 3.8 | 5 | 340 | 2G/4G/5G
CWN953 | SB | Outdoor | Mina | 21.4188 | 39.8927 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 40 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240 | 2G/4G
CWN959 | SB | Outdoor | Mina | 21.4178 | 39.9104 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240 | 2G/4G
CWN976 | SB | Outdoor | Mina | 21.4028 | 39.8975 | 0 | 0 | 100 | 25 | 0 | 18 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 17.4 | 18 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 40 min | 225 | 1.44 | 1.7778 | 80 | 4 | 5 | 240 | 2G/4G
CWN001 | SB | Outdoor | Arafat | 21.3373 | 39.9578 | 0 | 0 | 100 | 30 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 20.88 | 21 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G
CWN021 | SB | Shelter | Muzdalifah | 21.3934 | 39.9166 | 0 | 0 | 100 | 35 | 0 | 24 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 0 | 31.28 | 24.36 | 24 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 40 min | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 240 | 2G/4G
CWN002 | SB | Shelter | Mina | 21.4204 | 39.8714 | 0 | 0 | 100 | 35 | 0 | 19.2 | 36000 | 0 | 36000 | 0 | 190 | 3 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 24.36 | 19.2 | 29880 | 2.5021 | 29880 | 2.5021 | 285 | 14.25 | 0 hr 57 min | 240 | 1.536 | 1.1875 | 57 | 2.85 | 5 | 300 | 2G/4G/5G
CWN961 | SB | Outdoor | Mina | 21.3984 | 39.8973 | 0 | 0 | 100 | 45 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 31.32 | 21 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN997 | SB | Outdoor | Muzdalifah | 21.3831 | 39.9045 | 0 | 0 | 100 | 35 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 21 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN915 | SB | Shelter | Muzdalifah | 39.925555 | 39.925555 | 0 | 0 | 100 | 30 | 0 | 19 | 48000 | 0 | 48000 | 0 | 400 | 2 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 0 | 31.28 | 20.88 | 19 | 39840 | 3.3361 | 39840 | 3.3361 | 400 | 20 | 1 hr 20 min | 237.5 | 1.52 | 1.6842 | 80 | 4 | 5 | 300 | 2G/4G
CWN076 | SG | Shelter | Arafat | 21.3692 | 39.9771 | 35 | 0 | 0 | 0 | 0 | 18 | 36000 | 0 | 36000 | 0 | 200 | 7 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 24.36 | 0 | 0 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 700 | 35 | 2 hr 55 min | 225 | 1.44 | 3.1111 | 140 | 7 | 5 | 240 | 2G/4G
CWN083 | SG | Shelter | Arafat | 21.3314 | 39.9655 | 35 | 0 | 0 | 0 | 0 | 18 | 36000 | 0 | 36000 | 0 | 200 | 3 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 24.36 | 0 | 0 | 18 | 29880 | 2.5021 | 29880 | 2.5021 | 300 | 15 | 1 hr 15 min | 225 | 1.44 | 1.3333 | 60 | 3 | 5 | 240 | 2G/4G/5G
CWN050 | SG | Shelter | Arafat | 21.3854 | 40.0052 | 45 | 0 | 0 | 0 | 0 | 19.2 | 48000 | 0 | 48000 | 0 | 200 | 2 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 31.32 | 0 | 0 | 19.2 | 39840 | 3.3361 | 39840 | 3.3361 | 200 | 10 | 0 hr 40 min | 240 | 1.536 | 0.83333 | 40 | 2 | 5 | 300 | 2G/4G
CWN213 | SB | Outdoor | Muzdalifah | 39.9082 | 39.9082 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 11 min | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN101 | SG | Shelter | Muzdalifah | 21.3884 | 39.9277 | 45 | 0 | 0 | 0 | 0 | 23 | 36000 | 0 | 36000 | 0 | 200 | 5 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 0 | 23 | 29880 | 2.5021 | 29880 | 2.5021 | 500 | 25 | 1 hr 28 min | 287.5 | 1.84 | 1.7391 | 100 | 5 | 5 | 340 | 2G/4G/5G
CWN955 | SB | Outdoor | Muzdalifah | 39.8974 | 39.8974 | 0 | 0 | 100 | 30 | 0 | 21 | 10200 | 0 | 0 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 20.88 | 21 | 8466 | 1.4179 | 0 | 0 | 380 | 19 | 1 hr 7 min | 262.5 | 1.68 | 1.4476 | 76 | 3.8 | 5 | 340 | 2G/4G/5G
CWN994 | SG | Outdoor | Mina | 21.4235 | 39.8953 | 35 | 0 | 0 | 0 | 0 | 15 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 24.36 | 0 | 0 | 15 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 40 min | 187.5 | 1.2 | 2.1333 | 80 | 4 | 5 | 240 | 2G/4G/5G
CWN081 | SG | Shelter | Makkah Remote | 20.9935 | 39.5881 | 30 | 0 | 0 | 0 | 0 | 32 | 36000 | 0 | 36000 | 0 | 190 | 4 | 0 | 0.5 | 0.8 | 10.56 | 1.44 | 12 | 4913.28 | 20.88 | 0 | 0 | 32 | 29880 | 2.5021 | 29880 | 2.5021 | 380 | 19 | 1 hr 35 min | 400 | 2.56 | 0.95 | 76 | 3.8 | 5 | 240 | 2G/4G
CWN208 | SG | Outdoor | Muzdalifah | 39.9151 | 39.9151 | 35 | 0 | 0 | 0 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 24.36 | 0 | 0 | 21 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN022 | SG | Shelter | Arafat | 39.9895 | 39.9895 | 35 | 0 | 0 | 0 | 0 | 19 | 48000 | 0 | 48000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 24.36 | 0 | 0 | 19 | 39840 | 3.3361 | 39840 | 3.3361 | 400 | 20 | 1 hr 20 min | 237.5 | 1.52 | 1.6842 | 80 | 4 | 5 | 300 | 2G/4G/5G
CWN099 | SG | Shelter | Muzdalifah | 39.9013 | 39.9013 | 45 | 0 | 0 | 0 | 0 | 21 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 0 | 21 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G
CWN092 | SG | Shelter | Arafat | 39.9715 | 39.9715 | 45 | 0 | 0 | 0 | 0 | 19 | 36000 | 0 | 36000 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 13.2 | 1.8 | 15 | 6141.6 | 31.32 | 0 | 0 | 19 | 29880 | 2.5021 | 29880 | 2.5021 | 400 | 20 | 1 hr 20 min | 237.5 | 1.52 | 1.6842 | 80 | 4 | 5 | 300 | 2G/4G
CWN318 | SB | Outdoor | Muzdalifah | 39.9026 | 39.9026 | 0 | 0 | 100 | 35 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 21 | 8466 | 1.4179 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN062 | SG | Shelter | Muzdalifah | 39.8989 | 39.8989 | 45 | 0 | 0 | 0 | 0 | 21.6 | 36000 | 0 | 36000 | 0 | 425 | 2 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 0 | 21.6 | 29880 | 2.5021 | 29880 | 2.5021 | 425 | 21.25 | 1 hr 15 min | 270 | 1.728 | 1.5741 | 85 | 4.25 | 5 | 340 | 2G/4G/5G
CWN038 | SG | Shelter | Arafat | 39.9613 | 39.9613 | 45 | 0 | 0 | 0 | 0 | 23 | 48000 | 0 | 48000 | 0 | 200 | 7 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 31.32 | 0 | 0 | 23 | 39840 | 3.3361 | 39840 | 3.3361 | 700 | 35 | 2 hr 4 min | 287.5 | 1.84 | 2.4348 | 140 | 7 | 5 | 340 | 2G/4G
CWN205 | SB | Outdoor | Muzdalifah | 39.9146 | 39.9146 | 0 | 0 | 100 | 35 | 0 | 24 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 24.36 | 24 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 11 min | 300 | 1.92 | 1.3333 | 80 | 4 | 5 | 340 | 2G/4G/5G
CWN901 | SB | Outdoor | Arafat | 39.9895 | 39.9895 | 0 | 0 | 100 | 30 | 0 | 21 | 10200 | 0 | 0 | 0 | 200 | 4 | 0 | 0.5 | 0.8 | 14.96 | 2.04 | 17 | 6960.48 | 0 | 31.28 | 20.88 | 21 | 8466 | 0.70893 | 0 | 0 | 400 | 20 | 1 hr 11 min | 262.5 | 1.68 | 1.5238 | 80 | 4 | 5 | 340 | 2G/4G/5G